## Sheet1
SYSTEM VOLTAGE FOR FLOOR ONE | 120 Vrms
LOAD CALCULATIONS | CONTINUOUS | CONTINUOUS | NON - CONTINUOUS | NON-CONTINUOUS | CIRCUIT BREAKER SIZING | x1.25 | I | LINK
POWER (W) | Switch 1 - 10 LED x 15 W = 150 W | Switch 2 - 10 LED x 15 W = 150 W | 700 W | 400 W | CURRENT RATING | I = (1.25 x 1.25 A) + (1.25 x 1.25 A) + (1.25 x 5.83 A) + (1.25 x 3.33 A) | 14.56 A
CURRENT (A) | I = 150 W / 120 V = 1.25 A | I = 150 W / 120 V = 1.25 A | I = 700 W/ 120 V = 5.83 A | I = 400 W/ 120 V = 3.33 A
[5 empty] | CIRCUIT BREAKER | CATALOG INFORMATION | RATING | LINK
AREA OF OFFICE SPACE | TOTAL AREA | AREA OF CONTROL ROOM | AREA OFFICE |  | NOARK MCB B - CURVE | ONE POLE 15 A 277 VAC B1H1B15 | 15 A | https://na.noark-electric.com/wp-content/uploads/2023/05/noark-mcb-catalog.pdf
AREA OFFICE | 10.0 m x 8.5 m = 85m^2 | 2.4 m x 3.0 m = 7.2m^2 | 77.8mm^2
[5 empty] | SWITCHES | CATALOG INFORMATION | RATING | LINK
ILLUMENANCE (NORMAL CONDITIONS) | E [lux] = Φ [lumens] / A [m^2] | ILLUMENANCE FOR OFFICES |  |  | 2 x LEVITON RESIDENTIAL | ONE POLE 15 A 120 VAC SP15-R | 15 A | https://sunco.com/products/leviton-15-amp-decora-rocker-single-pole-ac-quiet-switch-grounding?variant=41039414165571
CALCULATIONS | (20 x 1500 lm) / 77.8mm^2 = 385.60 lux | 300 - 500 lux
[5 empty] | POWER WIRING SIZE | AWG SIZE | RATING | LINK
ILLUMENANCE (EMERGENCY CONDITIONS) | E [lux] = Φ [lumens] / A [m^2] | ILLUMENANCE FOR OFFICES |  |  | AWG 12 | FOR BREAKING CURRENT 15 A CHOOSE 12 AWG SINGLE CORE CROSS SECTIONAL AREA - 3.31mm^2 | 16 A - 20 A | https://www.cordial-cables.com/pdfs-produkte/cordial-awg-table.pdf
CALCULATIONS | (6 x 1500 lm) / 77.8mm^2 = 115.68 lux | FOR HIGH RISK AREA 115.68 lux ≈ 8 x 15 lux
[5 empty] | TEL WIRING SIZE | AWG SIZE | RATING | LINK
MINIMUM LUX FOR HIGH RISK AREAS | 15 lux |  |  |  | UTP CAT 6 AWG 23 | OUTER DIAMETER - 6.1mm, OUTER AREA = π x (d/2)^2 -> 29.22mm^2 | 1 A / CONDUCTOR | https://dlinkmea.com/me/image/catalog/catx/Cat6_u_utp_23awg_cable_new.pdf
[5 empty] | PVC CONDUITS | CALCULATION | MINIMUM CONDUIT INTERNAL AREA | CATALOG INFORMATION
[5 empty] | PHASE + NEUTAL / 1 CONDUIT | TOTAL AREA OF 12AWG WIRE WITH INSULATION - 8.58mm^2, 8.58mm^2 x 2 = 17.16mm^2, 17.16mm^2/0.31 = 55.35mm^2 | 55.35mm^2 -> 196mm^2 | https://blog.wavin.com/hubfs/Product%20Literature/PVC%20Schedule%2040/WA_PVC%20Scehd%2040%20Spec%20Sheet%209.2025.pdf?hsCtaTracking=37dce5c4-77a9-4651-b4e4-d95e2a0d76c6%7C01f96f2a-750b-4eb3-8ea0-ff3d268ad340
[5 empty] | PHASE / 1 CONDUIT | TOTAL AREA OF 12AWG WIRE WITH INSULATION - 8.58mm^2, 8.58mm^2/0.53 = 16.19mm^2 | 16.19mm^2 -> 196mm^2 | N/A
[5 empty] | 2 x UTP CAT 6 / 1 CONDUIT | TOTAL AREA - 29.22mm^2, 29.22mm^2/0.31 = 94.23mm^2, 94.23mm^2/343.99mm^2 = < 30% OF 3/4 INCH CONDUIT | 94.23mm^2 -> 343.99mm^2 | https://blog.wavin.com/hubfs/Product%20Literature/PVC%20Schedule%2040/WA_PVC%20Scehd%2040%20Spec%20Sheet%209.2025.pdf?hsCtaTracking=37dce5c4-77a9-4651-b4e4-d95e2a0d76c6%7C01f96f2a-750b-4eb3-8ea0-ff3d268ad340
20 x 15 W 1500 LUMENS PHILLIPS LED LIGHTS
[7 empty] | LIGHT LOADS | https://build-station.com/en/15w-led-anti-glare-recessed-ceiling-lights-cut-size-100mm-white/p21795597?srsltid=AfmBOoqCAXnAuvlzSwgSSf6cnL0LCnAN1uZNe5C82E-4VEbQRqJnCPK2
[7 empty] | 15 W 1500 LUMENS | https://optonica.bg/en/product/led-luna-15w-1500lm-sst-cri90-cherno-tyalo-bridgelux-chip/